{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":24,"n_cols":10,"rows_kept":24,"merged":[[1,0,1,9],[23,1,23,10]],"flags":["formulas_cached_only"]}
["附件1"]
["2022年防爆电气产品质量国家监督抽查不合格产品及企业名单"]
["序号","产品种类","标称生产单位","标称生产单位所在地","产品名称","规格型号","生产日期/批号","主要不合格项目","承检机构","备注"]
[1,"防爆灯具","江苏靖瑞麟防爆电气科技有限公司","江苏省","LED防爆防腐灯","RLBZD-50W   AC220V   50W",2022.07,"抗冲击试验,非铠装电缆和带编织覆盖层电缆的夹紧试验,隔爆外壳引入装置的附加要求,隔爆接合面,外壳耐压试验","南阳防爆电气研究所有限公司(国家防爆电气产品质量检验检测中心)"]
[2,"防爆灯具","江苏兆昌防爆电器有限公司","江苏省","LED防爆灯","BAT95-X 85～ 265V","2022.09.01","非铠装电缆和带编织覆盖层电缆的夹紧试验","南阳防爆电气研究所有限公司(国家防爆电气产品质量检验检测中心)"]
[3,"防爆灯具","淮北星光照明科技有限公司","安徽省","矿用隔爆型荧光灯","DGS24/127Y(A)","2022.03","抗冲击试验","初检机构：南阳防爆电气研究所有限公司(国家防爆电气产品质量检验检测中心)\n复检机构：中海油天津化工研究设计院有限公司（国家防爆产品质量检验检测中心（天津））","复检仍不合格"]
[4,"防爆灯具","中山市松吉照明科技有限公司","广东省","免维护LED防爆灯","BAD92 220V 50W","2022.3","隔爆接合面,外壳耐压试验","南阳防爆电气研究所有限公司(国家防爆电气产品质量检验检测中心)"]
[5,"防爆灯具","深圳瑞朗特防爆车辆有限公司","广东省","隔爆型防爆LED灯","BAK80  DC12V  9W","2022.8","隔爆接合面","南阳防爆电气研究所有限公司(国家防爆电气产品质量检验检测中心)"]
[6,"防爆电机","南京德拜自动化科技有限公司","江苏省","防爆交流伺服电机","90DB100C","2022.08.20","隔爆接合面","中海油天津化工研究设计院有限公司（国家防爆产品质量检验检测中心（天津））"]
[7,"防爆电机","江苏世隆电机有限公司","江苏省","高效率隔爆型三相异步电动机","YBX3-112M-4  4kW  380/660V","2022.08","隔爆接合面","中海油天津化工研究设计院有限公司（国家防爆产品质量检验检测中心（天津））"]
[8,"防爆电机","浙江沪新防爆电机有限公司","浙江省","高效率隔爆型三相异步电动机","YBX3-80M2-4 380V 0.75kW","2022年5月","隔爆接合面","中海油天津化工研究设计院有限公司（国家防爆产品质量检验检测中心（天津））"]
[9,"防爆电机","浙江浙凌机电有限公司","浙江省","高效率隔爆型三相异步电动机","YBX3-132S2-2，7.5kW，380/660V","2022年7月","隔爆接合面","中海油天津化工研究设计院有限公司（国家防爆产品质量检验检测中心（天津））"]
[10,"防爆电机","温州申银防爆电机有限公司","浙江省","隔爆型三相异步电动机","YBM-112M-2,4kW,380/660V","2022年8月","隔爆接合面","初检机构：中海油天津化工研究设计院有限公司（国家防爆产品质量检验检测中心（天津））\n复检机构：南阳防爆电气研究所有限公司（国家防爆电气产品质量监督检验中心）","复检仍不合格"]
[11,"防爆电机","山东力久特种电机股份有限公司","山东省","高效率隔爆型三相异步电动机","YBX3-80M2-4 0.75kW 380V","/","隔爆接合面","中海油天津化工研究设计院有限公司（国家防爆产品质量检验检测中心（天津））"]
[12,"防爆电机","西安泰富西玛电机有限公司","陕西省","高效率隔爆型三相异步电动机","YBX4-132S-4  5.5kW  380V","2022.07","隔爆接合面","中海油天津化工研究设计院有限公司（国家防爆产品质量检验检测中心（天津））"]
[13,"防爆电器","沈阳广角成套电器股份有限公司","辽宁省","矿用隔爆型转换开关","KBH-10/127  127V","2022.08","非铠装电缆和带编织覆盖层电缆的夹紧试验","南阳防爆电气研究所有限公司(国家防爆电气产品质量检验检测中心)"]
[14,"防爆电器","启东市科安防爆电器通讯有限公司","江苏省","防爆一体化云台摄像仪","KTY-01  220VAC","2022.03","隔爆接合面","中海油天津化工研究设计院有限公司（国家防爆产品质量检验检测中心（天津））"]
[15,"防爆电器","常州市龙安电子有限公司","江苏省","LAJB500 防爆控制箱","LAJB500   AC220V   额定电流≤1A",2022.7,"隔爆接合面","南阳防爆电气研究所有限公司(国家防爆电气产品质量检验检测中心)"]
[16,"防爆电器","上海福泽工业自动化设备有限公司江阴分公司","江苏省","复合防爆扬声器","EXYS03-B  120V",2022.09,"非铠装电缆和带编织覆盖层电缆的夹紧试验,隔爆接合面","南阳防爆电气研究所有限公司(国家防爆电气产品质量检验检测中心)"]
[17,"防爆电器","浙江德力装备有限公司","浙江省","防爆型电气控制箱","BXK68B/1.5","2022年8月","隔爆接合面","南阳防爆电气研究所有限公司(国家防爆电气产品质量检验检测中心)"]
[18,"防爆电器","浙江九诺电力科技有限公司","浙江省","防爆控制箱（操作柱）","BXK  220V/380V  100A",2022.8,"电气间隙,爬电距离,非铠装电缆和带编织覆盖层电缆的夹紧试验","中海油天津化工研究设计院有限公司（国家防爆产品质量检验检测中心（天津））"]
[19,"防爆电器","浙江广顺防爆电气有限公司","浙江省","防爆接线盒","AH-D/3/4  220/380V  20A","2022.8","非铠装电缆和带编织覆盖层电缆的夹紧试验","南阳防爆电气研究所有限公司(国家防爆电气产品质量检验检测中心)"]
[20,"防爆电器","淮南市润金工矿机电有限公司","安徽省","矿用隔爆型电动球阀","DFB20/10 AC127V",2022.08,"隔爆接合面","中海油天津化工研究设计院有限公司（国家防爆产品质量检验检测中心（天津））"]
[null,"注：1.按产品及行政区域排序。\n    2.复检仍不合格，指产品初检不合格，企业提出复检申请，经复检产品仍不合格。"]